## Standard Master
# | Document | Page number | Reviewer | Reference e.g. paragraph number, section, figure/table no. | Current text/issue | Proposed change | Review status | Comment | Proposed alternative
1 | Test Standard | All | FV | Version number | Front page, section headers, footers all have "Version 3: 2023" | "Version 3.1: 2026" | To review
2 | Test Standard | Throughout | FV | Minor edits | Minor edits are track changed throughout, rectifying typos/formatting etc | To amend as per tracked changes in the document. | To review
3 | Test Standard | Throughout | FV | Formatting | Formatting within word document provided is not consistent with published document | Formatting to be rectified in line with published version | To review
4 | Test Standard | Throughout | FV | References to sections/figures/tables |  | To be updated if sections/tables/figures are deleted/changed | To review
5 | Test Standard | 2 | FV | Revision History | New revision to add | V3-Rev002 Amendments as detailed in [external document reference] Technical Committee Steering Group [Date of release] | To review
6 | Test Standard | 3 | FV | Steering Committee membership | To ensure correct membership | "Established as part of a UK government research project into heat network efficiency, the Test Standard was, and continues to be, developed under the auspices of a steering group of industry experts: • Kevin Morrissey (BESA) (Chair) • Gareth Jones (FairHeat) (Vice-Chair) • Keegan Farrelly (BESA) (Secretariat) • Ian Spencer (Vital Energi) (MEHNA manufacturer’s representative) • Josu Aurrekoetxea (Hemiko) • Pete Mills (Bosch) (MEHNA manufacturer’s representative) • Phil Jones (representing CIBSE & DESNZ) • Steve McConnell (MEHNA) Previous members of the Steering Committee who contributed to the development of the third version of the Test Standard should also have their contributions noted: • Amita Mehta (Peabody) • Graeme Fox (BESA) • Stephen Hutchins (EQUANS) • Tim Starley-Grainger (LB of Haringey)" | To review
7 | Test Standard | 3 | FV | Technical Committee membership | To ensure correct membership | "The detailed work that underpins the Test Standard, and the changes that have been made throughout the project, has been carried out by a technical committee of industry experts: • Gareth Jones (FairHeat) (Chair) • Valeria Khnykina (FVB) (Vice-Chair) • Freddie Valletta (FairHeat) (Technical Lead) • Ethan St Catherine (FairHeat) (Secretariat) • Adam Gleeson (Enertek) • Christer Frennfelt (SWEP) • Ian Robinson (Baxi) (MEHNA manufacturer’s representative) • Josu Aurrekoetxea (Hemiko) • Keegan Farrelly (BESA) • Kevin Morrissey (BESA) • Neil Gatland (Herz) (MEHNA manufacturer’s representative) • Paul Needley (Enertek) • Simon Broxham (Enertek) • Tom Naughton (FairHeat) Previous members of the Technical Committee who contributed to the development of the third version of the Test Standard should also have their contributions noted: • Colin Judd (BSRIA) • Dmitriy Mostovoy (Metropolitan) • Graeme Fox (BESA) • Henrik Persson (RISE) • Robert Hunter (Orka Building Services) • Dr Steffan Cook (BIA Energy Consulting) • Wayne Early (Buro Happold)" | To review
8 | Test Standard | 4 | FV | Acknowledgements | To update wording | • Gareth Jones (Chair) • Valeria Khnykina (Vice-Chair) • Phil Jones (Lead Editor) • Freddie Valletta (Technical Editor) • Tom Naughton • Josu Aurrekoetxea • Christer Frennfelt • Ian Robinson • Wayne Early • Samuel Bryce | To review
9 | Test Standard | 5 | FV | Foreword | To update wording | See edits in marked up doc | To review
10 | Test Standard | 6 | FV | Contents |  | To update based on other changes to the document. | To review
11 | Test Standard | 7, 8 | FV | Introduction | To update wording | See edits in marked up doc (note that the document provided misses text that is included in the standard and needs to be readded). After text within missing blue box, insert: “The relevant version of each module document for each version of the Test Standard is also published on the BESA website.” | To review
12 | Test Standard | 10 | FV | Voluntary section | To update wording to include direction of travel | See edits in marked up doc | To review
13 | Test Standard | 11 | FV | PCDB |  | "At the time of the release of this document, the PCDB process is still to be confirmed but it is intended to be made available to manufacturers before the end of 2023" to be deleted | To review
14 | Test Standard | 11 | FV | Section 2 additional docs to mention |  | Wording on additional documentation to refer to, to confirm wording and which ones with Phil e.g.: complaints procedure query procedure Results interpretation mehna hiu | To review
15 | Test Standard | 12, 13 | FV | Major changes | Text and table on pg 12, 13 can be deleted as there are no major changes in this version | To delete text and table on pg 12 & 13 Section to be renamed "Summary of Pass/Fail Thresholds" | To review
16 | Test Standard | 14 | FV | Pass/fail thresholds list | Addition of new pass/fail thresholds in list | "Indirect space heating average temperature (introduced in V3.1) Indirect and Direct space heating mix down temperature stability (indirect stability introduced in V3.1)" | To review
17 | Test Standard | 16 | FV | Pass/fail thresholds explanations | Addition of new pass/fail thresholds in text | See edits in marked up doc for "Indirect space heating average temperature" and "Space Heating (Indirect) Temperature Stability" | To review
18 | Test Standard | 16 | FV | VWARTs | Amendment of DHW VWART Amendment of Space Heating (indirect) VWART | High temp to 20 and low temp to 25 Both 40 to 37 | To review
19 | Test Standard | 17,18 | FV | Table 3 summary of pass/fail | Adddition of new pass/fail criteria | See edits in marked up doc (11a/b vwart changes 01a-01f temp stability and VWARTs) page breaks to fix | To review
20 | Test Standard | 19 & 49 | FV | Tables 3 & 11 | Wording for test 13 pass/fail criterion is unclear: “DHW (at t₃₂) is less than 50 °C ± 1.0 °C (to one decimal place)…” | “DHW (at t32) is not maintained to 50 °C ± 1.0 °C at 0.13 l/s flow rate…” | To review
21 | Test Standard | 20 | FV | Terminology | Updates to TS1 terminology | See edits in marked up doc | To review
22 | Test Standard | 22 | FV | 4.13 | fix typo | "it is impossible" to "it impossible" | To review
23 | Test Standard | 22 | FV | 4.14 | Additional clarity on assessment procedure for repeating tests | See edits in marked up doc | To review
24 | Test Standard | 23 | FV | 4.15 | Addition of V3.1 | See edits in marked up doc | To review
25 | Test Standard | 25-27 | FV | HIUs in scope |  | remove repeated table headings on each page | To review
26 | Test Standard | 28 | FV | 5.2 |  | Add: "• Confirmation of specific HIU set up and commissioning parameters" | To review
27 | Test Standard | 28 | FV | 5.3 | Inclusion of heating temp stability | See edits in marked up doc | To review
28 | Test Standard | 29 | FV | 5.7 |  | "plate heat exchanger" | To review
29 | Test Standard | 31 | FV | 5.12 fig 2 | Incorrect label included | Correct label to be inserted | To review
30 | Test Standard | 31 | FV | 5.14 | Added additional guidance on comparisons. | See edits in marked up doc | To review
31 | Test Standard | 32 | FV | 5.15 | Update validity of previous test regimes | See edits in marked up doc | To review
32 | Test Standard | 33, 56, 57, 58, 60, 63, 70-73 | FV | Figures 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13 | Diagram formatting is not consistent with the published version | To be rectified | To review
33 | Test Standard | 37 | FV | 8.3 | Additional clarity on assessment procedure for repeating tests | See edits in marked up doc | To review
34 | Test Standard | 39 | FV | 9.1 | Previous comment left in on word doc | To be deleted as per edits | To review
35 | Test Standard | 37-43 | FV | 8-10 Tables 6-10 | Sections 8, 9 & 10 and tables 6, 7, 8, 9 & 10 should be able to be combined and consolidated into a single section and fewer tables and text. Table 6 is the most expendable and the sections and text will need shifting round. | To be drafted | To review
36 | Test Standard | 41, 42 | FV | Table 8 | Coloured text no longer required Formatting and alignment doesn't match with published doc | Coloured text to be removed Formatting and text alignment to be updated in line with published doc | To review
37 | Test Standard | 42 | FV | Table 8 | Heating module 7 incorrectly named as hot water module 1 (not in published doc but present in this doc | HOT WATER MODULE 7-DH70-KWarm | To review
38 | Test Standard | 43 | FV | Manufacturer's test menu | Text present that doesn't add anything to the section | "The module selection menu is shown in section 10, and the detailed tests in each module are provided in separate documents: • MODULE M1 Space Heating • MODULE M2 Space Heating • MODULE M3 Space Heating • MODULE M4 Space Heating • MODULE M5 Space Heating • MODULE M6 Space Heating • MODULE M7 DHW • MODULE M8 DHW • MODULE M9 DHW • MODULE M10 DHW" TO BE DELETED | To review
39 | Test Standard | 43 | FV | Manufacturer's test menu | Text to be added to confirm that relevant module document versions associated with each test standard version will be published on the besa website. | Text to add to "manufacturers test menu" section: "• The specification for each of the modules are contained within separate documents for each module. The relevant version of each module document for each version of the Test Standard is published on the BESA HIU website." | To review
40 | Test Standard | 44 | FV | VWART pass/fail | Confirm current editions | See edits in marked up doc | To review
41 | Test Standard | 46 | FV | 11.4 | Test Reporting and Assessment Criteria heading | can be deleted | To review
42 | Test Standard | 46 | FV | 11.4 | Additional clairty on reporting, which will facilitate Table 11 to be deleted | See edits in marked up doc | To review
43 | Test Standard | 46-51 | FV | Table 11 | Table 11 is repeated within the module documents and will need updating every time a module is updated, therefore can be deleted | To be deleted | To review
44 | Test Standard | 52 | FV | 12 | Additional docs to reference | Phil to confim which additional docs need to be referenced e.g: e.g.: V3 of test TS1 HNTAS docs Bs8635 part 2 Interpretation doc Complaints/queries process MEHNA guide MMS | To review
45 | Test Standard | 53 | FV | App A | Additional definitions to add | Phil to confirm which HNTAS specific wording/definitions need to be added | To review
46 | Test Standard | 54 & 65 | FV | App A - Abbreviations Appendix C - Nomenclature | Subscripts for H₂ and H₃ for space heating and DHW power reversed "H₂ Arithmetic mean of DHW power recorded during test" "H₃ Arithmetic mean of space heating power recorded during test" | Reverse definitions so rows in table read: "H₂ Arithmetic mean of space heating power recorded during test" "H₃ Arithmetic mean of DHW power recorded during test" | To review
47 | Test Standard | 57 | FV | B2.4 |  | tb1 to be subscript | To review
48 | Test Standard | 57 | FV | Figure 5 | Clarity requested to be added to diagram to fully indicate what sections A and B are referring to. | Diagram to be amended | To review
49 | Test Standard | 58 | FV | B3.1, B3.2 plus Figures 6 & 7 |  | Formatting to be rectified | To review
50 | Test Standard | 59 | FV | Appendix B4.2, Table 13 | - Incorrect reporting precision for differential pressure given (1 d.p. not nearest whole number) - Missing precision for power, H - Volume flow deviation indicated as +/- 5 K in this doc but not in main doc | - Change from 1 d.p. to nearest whole number (change from "1.0 kPa" to "1 kPa") - Include row in table for the reporting precision of power, which is 0.1 kW (except in test 21a/b when 0.01 kW is required for overall HIU energy losses) - ±5K to change to ±5% | To review
51 | Test Standard | 60, 61 | FV | B4.4-4.18 |  | Line spacing and alignment to rectify | To review
52 | Test Standard | 63 | FV | Figure 9 | Graph has errors that have previously been picked up in an addendum that has been published on the BESA website | See addendum document with amended graph in with correct dP profiles and updated increments on both axes. Also copied to the right | To review
53 | Test Standard | 63 | FV | B7.2 | Slight amend to Water Regulation certification process as previously agreed by the Technical Committee | See edits in marked up doc | To review
54 | Test Standard | 64 | FV | Appendix C Nomenclature | Nomenclature repeated in App A | Nomenclature table to delete | To review
55 | Test Standard | 65-69 | FV | Appendix C methodology | Formatting not consistent with published document | Formatting to amend | To review
56 | Test Standard | 70-73 | FV | Figures 10, 11, 12, 13 | Diagram formatting is inconsistent with published version Phil mentioned an updated version might be contained within updated HNTAS documentation which should be utilised here. | Phil to confirm updated version of diagrams. | To review
57 | Test Standard | 74 | FV | App E |  | To update based on other changes to the document. | To review
58 | Test Standard | 75 | FV | Final page |  | Format to amend to align with published document | To review

## Modules
# | Document | Page number | Reviewer | Reference e.g. paragraph number, section, figure/table no. | Cuurent text/issue | Proposed change | Open/Closed | Comment | Proposed alternative
1 | M1-10 | All | FV | Version number | Front page, section headers, footers all have "Version 1: 2023" | "Version 1.1: 2026" | To review
2 | M1-10 | Throughout | FV | Minor edits | Minor edits are track changed throughout, rectifying typos/formatting etc | To amend as per tracked changes in the documents (e.g. spelling, formatting, subscripts) | To review
3 | M1-10 | Throughout | FV | Formatting | Formatting within word document provided is not consistent with published document | Formatting to be rectified in line with published versions (particularly with paragraph numbers not aligning with their paragraphs) | To review
4 | M1-10 | Throughout | FV | References to sections/figures/tables |  | To be updated if sections/tables/figures are deleted/changed | To review
5 | M1-10 | 1 | FV | Revision History | New revision to add | V1-Rev002 Amendments as detailed in [external document reference] Technical Committee Steering Group [Date of release] | To review
6 | M1-10 | 1 | FV | 1. Introduction |  | Text to add at end of section: "The relevant version of the Test Standard that this sub-document applies to is detailed on the BESA HIU website www.thebesa.com/heating-interface-units." | To review
7 | M1-10 | Throughout | FV | Test output sections |  | "A test report shall be prepared using the standardised BESA output template available to download from the BESA HIU website. The test will provide the following outputs:" | To review
8 | M1 | 2,3 | FV | M1.3.7 - M1.3.10 | Amended text to align with updated criteria. | Formatting won't allow for easy amendments. Amendments as detailed in separate document: “HIU Test Standard 2026 version Modules amended text” | To review
9 | M1 | 3 | FV | Pass/fail criteria | Amended VWART criteria Additional pass/fail criteria | Fail if the VWART is above 37ºC (to one decimal point). Fail if the space heating ﬂow temperature, t22, is not maintained at 55°C ±5.0°C (to one decimal place) for more than one second. Fail if the average space heating flow temperature, t22, across the test is not 55°C ±0.5°C (to one decimal place) (01c only) Fail if the average space heating flow temperature, t22, across the test is not 55°C -0.5°C/+2.0°C (to one decimal place) (01a and 01b) | To review
10 | M1 | 3 | FV | Best practice criteria | Amended best practice criteria | Best practice if the VWART is less than or equal to 36ºC (to one decimal point). Best practice if the average space heating flow temperature, t22, across all three tests is within 55°C ±0.5°C. | To review
11 | M2 | 1,2 | FV | M2.3.1, M2.3.2 | Order of text does not match M1 | Order of text to match order of text in sections M1.3.1, M1.3.2 for consistency. I would do it myself, but the formatting is resulting in difficulty moving text around. Paragraphs in order go: M2.3.1 Objective… Note: The static tests… M2.3.2 The primary differential… Note that in plotting... | To review
12 | M1 | 2,3 | FV | M2.3.7 - M2.3.10 | Amended text to align with updated criteria. | Formatting won't allow for easy amendments. Amendments as detailed in separate document: “HIU Test Standard 2026 version Modules amended text” | To review
13 | M2 | 3 | FV | Pass/fail criteria | Amended VWART criteria Additional pass/fail criteria | Fail if the VWART is above 37ºC (to one decimal point). Fail if the space heating ﬂow temperature, t22, is not maintained at 45°C ±5.0°C (to one decimal place) for more than one second. Fail if the average space heating flow temperature, t22, across the test is not 45°C ±0.5°C (to one decimal place) (01f only) Fail if the average space heating flow temperature, t22, across the test is not 45°C -0.5°C/+2.0°C (to one decimal place) (01d and 01e) | To review |  |  | 0.095694 | 0.047847
14 | M2 | 3 | FV | Best practice criteria | Amended best practice criteria | Best practice if the VWART is less than or equal to 36ºC (to one decimal point). Best practice if the average space heating flow temperature, t22, across all three tests is within 45°C ±0.5°C. | To review |  |  | 0.023923 | 0.011962
15 | M3 | 1,2 | FV | M3.3.1, M3.3.2 | Aid consistency between docs | Order of text to match order of text in other SH modules for consistency. I would do it myself, but the formatting is resulting in difficulty moving text around. Paragraphs in order go: M3.3.1 Objective… Note: The static tests data… M3.3.2 The primary differential pressure... Note that in plotting... | To review |  |  | 0.011962 | 0.0059809
16 | M3 | 4, 5 | FV | Figures 3 and 4 | Graph formatting is inconsistent with that in published version Flow rate shown is incorrect Flow rate should be a dashed (not dotted or solid) line dP should be a dotted line | Graph formatting to be rectified Ensure flow rate depicted is as per 02c, i.e. 0.027 l/s Amend flow rate so that it’s a dashed line and dP so it's dotted line | To review
17 | M3 | 5 | FV | M3.3.13, M3.3.14 | Text missing from published version | See edits in marked up doc | To review
18 | M4 | 1 | FV | M4.3.1 | Aid consistency between docs | Order of text to match order of text in other SH modules for consistency. I would do it myself, but the formatting is resulting in difficulty moving text around. Paragraphs in order go: M4.3.1 Objective… Note: The static tests data… M4.3.2 The primary differential pressure shall vary between 50 kPa and 200 kPa. The test rig shall control primary differential pressure to the set point ±4%. Note that in plotting... | To review
19 | M4 | 4,5 | FV | Figures 3 and 4 | Graph formatting is inconsistent with that in published version Flow rate shown is incorrect Flow rate should be a dashed (not dotted or solid) line dP should be a dotted line Graphs to be amended to reflect 02f not 02c | Graph formatting to be rectified Ensure flow rate depicted is as per 02f, i.e. 0.048 l/s Amend flow rate so that it’s a dashed line and dP so it's dotted line | To review
20 | M5 | 1 | FV | 2 scope | Missing text | Text to add: "This document covers the tests required for registration under" | To review
21 | M5 | 1,2 | FV | M5.3.1, M5.3.2 | Aid consistency between docs | Order of text to match order of text in other SH modules for consistency. I would do it myself, but the formatting is resulting in difficulty moving text around. Paragraphs in order go: M5.3.1 Objective… Note: The static tests data… M5.3.2 The primary differential pressure... Note that in plotting... | To review |  |  |  | 0.095694
22 | M5 | 4, 5 | FV | Figures 3 and 4 | Graph formatting is inconsistent with that in published version Flow rate shown is incorrect Flow rate should be a dashed (not dotted or solid) line dP should be a dotted line | Graph formatting to be rectified Ensure flow rate depicted is as per 03c, i.e. 0.048 l/s Amend flow rate so that it’s a dashed line and dP so it's dotted line | To review |  |  |  | 0.047847
23 | M6 | 1,2 | FV | M6.3.1, M6.3.2 | Aid consistency between docs | Order of text to match order of text in other SH modules for consistency. I would do it myself, but the formatting is resulting in difficulty moving text around. Paragraphs in order go: M6.3.1 Objective… Note: The static tests data… M6.3.2 The primary differential pressure... Note that in plotting... | To review
24 | M6 | 4,5 | FV | Figures 3 and 4 | Graph formatting is inconsistent with that in published version Flow rate shown is incorrect Flow rate should be a dashed (not dotted or solid) line dP should be a dotted line Graph to be amended to reflect 03f not 03c | Graph formatting to be rectified Ensure space heating flow rate depicted is as per 03f, i.e. 0.096 l/s Ensure primary flow rate depicted is as per 03f, i.e. 0.048 l/s Ensure primary and space heating flow temperatures are as per 03f, i.e. 55C and 45C respectively Amend flow rate so that it’s a dashed line and dP so it's dotted line | To review
25 | M3, M4, M5, M6 | 2 or 3 | FV | Table 1 |  | Headings to update for clarity Add 0 to test name in caption to ensure correct reference e.g. 02a, not 2a | To review
26 | M9 | 10 | FV | Test 13 P/F | VWART p/f included incorrectly in word doc (but isn't in publihsed version) | VWART criteria to be deleted | To review
27 | M9 | 13 | FV | Test 32 | Duplication of start of section of Test 32 | Delete duplication | To review
28 | M10 | 4, 9 | FV | Figure 1 and 2 | Wrong module referenced in Figure caption: "M9 Figure…" | Change "M9" to "M10" | To review
29 | M10 | 12 | FV | M10.3.47 | Duplication of one clause and omission of another | Replace 10.3.47 with: "For this test the DHW set point shall be 50°C." | To review
30 | M7, M8 | 13 | FV | Test 21 BP | VWART best practice was agreed to be removed | Removed VWART best practice and amended wording of heat loss best practice | To review
31 | M7, M8 | 15 | FV | Test 22 BP |  | Amended best practice wording | To review
32 | M9, M10 | 13 | FV | Test 31 BP |  | Amended best practice wording | To review
33 | M9, M10 | 15 | FV | Test 32 BP |  | Amended best practice wording | To review
34 | M7, M8, M9, M10 | 1 | FV | Rev history | Revision history table covers up text and isn't inserted in the doc in the same way as M1-6 | To rectify | To review
35 | M7, M8, M9, M10 | 4 | FV | Figure 1 | Test 11 graph has errors that have previously been picked up in an addendum that has been published on the BESA website | See addendum document with amended graph in with correct dP profiles and updated increments on both axes. Also copied to the right | To review
36 | M7, M8, M9, M10 | 4, 6, 9, 12, 14 | FV | M7.3, M8.3, M9.3, M10.3 Tests 11, 12, 13, 21, 22 |  | "The HIU outer case shall be in place for this test. No heating shall be enabled during this test." to be a new paragraph number in all sections | To review
37 | M7, M8, M9, M10 | 5 | FV | Test 11 P/F |  | Amended VWART pass/fail number | To review
38 | M7, M8, M9, M10 | 5 | FV | Test 11 BP |  | Amended VWART best practice number and wording | To review
39 | M7, M8, M9, M10 | 9 | FV | Figure 2 |  | To rectify formatting in line with publihsed version | To review
40 | M7, M8, M9, M10 | 10 | FV | Test 13 P/F | Wording for test 13 pass/fail criterion is unclear: “DHW (at t₃₂) is less than 50 °C ± 1.0 °C (to one decimal place)…” | "Fail if DHW (at t32) is not maintained at 50°C ±1.0°C..." | To review