****

**Assumption Change Control Sheet**

|  |  |
| --- | --- |
| **Test** | 3a, 3b Low flow DHW Tests |
| **Assumption** | 23. Duration of low flow test |

|  |  |
| --- | --- |
| Change Originator | Martin Crane |
| **Change Request No.** | 014 |
| Date of Request | 17/12/2019 |
| Proposed Change to Assumption? | **No** |

|  |
| --- |
| **Proposed Approach**  Retain current 180 second test duration. |
| **Rationale (underlying basis for assumption)**  Based on test undertaken to date HIU tend to have stabilised before 180 seconds. Hence 180 seconds is considered sufficient time to show any untoward behaviour. |
| **Impact of Change (e.g. implications for test rig)**  N/A |

|  |  |
| --- | --- |
| CHANGE EVALUATION | |
| Date Evaluated | 17/12/2019 |
| Additional Information Required? | N |
| Modification to Proposed Approach? | N |
| Details | |
| Signed-off | Y |