****

**Assumption Change Control Sheet**

|  |  |
| --- | --- |
| **Test** | 1a, - 1f, Space heating Tests |
| **Assumption** | 11. Permitted variation in secondary flow temperature, t22. |

|  |  |
| --- | --- |
| Change Originator | Martin Crane |
| **Change Request No.** | 009 |
| Date of Request | 17/12/2019 |
| Proposed Change to Assumption? | **No** |

|  |
| --- |
| **Proposed Approach**  Retain permitted variation of +/- 0.5°C |
| **Rationale (underlying basis for assumption)**  0.5°C is the balance between a practically achievable tolerance on the test rig and the accuracy / consistency of the resulting return temperature measurement, as discussed with Test Houses. |
| **Impact of Change (e.g. implications for test rig)**  N/A |

|  |  |
| --- | --- |
| CHANGE EVALUATION | |
| Date Evaluated | 17/12/2019 |
| Additional Information Required? | N |
| Modification to Proposed Approach? | N |
| Details | |
| Signed-off | Y |