

|  |  |  |
| --- | --- | --- |
| **Change Note** | | **CN-045** |
| **Change to:** Technical Assumption46 | | |
| **Description:** Inner diameter for piping of HIU fittings | | |
| **References:** Test regime paragraph 2.5c, all Tests | | |
| **Change originator:** FV | | **Date of request:** 30/06/21 |
| **Rev:** 01 | **Date authored:** 21/09/21 | **Proposed change to assumption:** N |

1. Proposed Approach

Inner diameter for piping of HIU fittings to be between 20-25 mm.

Criteria as previously.

1. Rationale (underlying basis for the change)

To match up closely with expected HIU pipework diameters to minimise flow disturbances or pressure losses.

1. Impact of change (e.g. implications for test rig)

N/A

|  |  |  |  |
| --- | --- | --- | --- |
| **Evaluation of change** | | | |
| **Date evaluated:** 30/06/21 | **Those present:** GJ, RH, SC, MO & FV | **Additional info required?:** N | **Modification to proposed approach?:** N |
| **Details:** Confirmation of HIU pipework fittings inner diameter | | | |
| **Signed off: Yes** | | | |