****

**Assumption Change Control Sheet**

|  |  |
| --- | --- |
| **Test** | 2a, 2b Dynamic DHW Tests |
| **Assumption** | 21. Dynamic test including both on/ off and change of flow. |

|  |  |
| --- | --- |
| Change Originator | Martin Crane |
| **Change Request No.** | 013 |
| Date of Request | 17/12/2019 |
| Proposed Change to Assumption? | **No** |

|  |
| --- |
| **Proposed Approach**  Retain current dynamic test profile that include both on/off and change of DHW flowrate. |
| **Rationale (underlying basis for assumption)**  Many HIUs seem to respond differently when changing from 0.13 to 0.06 l/sec and back again as opposed to on/off. Important consideration for resident comfort and safety. |
| **Impact of Change (e.g. implications for test rig)**  N/A |

|  |  |
| --- | --- |
| CHANGE EVALUATION | |
| Date Evaluated | 17/12/2019 |
| Additional Information Required? | N |
| Modification to Proposed Approach? | N |
| Details | |
| Signed-off | Y |