****

**Assumption Change Control Sheet**

|  |  |
| --- | --- |
| **Test** | 1a, - 1f, Space heating Tests |
| **Assumption** | 14. Test sample duration |

|  |  |
| --- | --- |
| Change Originator | Tom Naughton |
| **Change Request No.** | 012 |
| Date of Request | 03/01/2020 |
| Proposed Change to Assumption? | **No** |

|  |
| --- |
| **Proposed Approach**  300 seconds |
| **Rationale (underlying basis for assumption)**  The duration was based on observations during the six original SBRI HIU tests. It was evaluated that this was sufficient time to capture any cyclical variability in primary return temperature observed from the tested HIUs.  All HIUs tested since have not shown any greater variability in primary return temperatures and therefore, there is no rationale for changing this value. |
| **Impact of Change (e.g. implications for test rig)**  N/A |

|  |  |
| --- | --- |
| CHANGE EVALUATION | |
| Date Evaluated | 23/07/2020 |
| Additional Information Required? | N |
| Modification to Proposed Approach? | N |
| Details | |
| Signed-off | Y |