| Technical Note |  |  | TN-025 |  |
| --- | --- | --- | --- | --- |
| Test: All tests |  |  | Test no.: |  |
| Assumption: Flow restrictor pressure loss |  |  | Assumption no: 58 |  |
| Rev: 03 | Date: 18/01/2022 | Author: Valeria Khnykina |  | Checked: Tom Naughton |

# Introduction

# Consideration 1

A number of heat meters types and manufacturers have been reviewed and the pressure loss compared with the test assumption.

Summary of results:

|  | Qp | Nominal Diameter | Flow rate, m3/h | Pressure loss, mbar | Type |
| --- | --- | --- | --- | --- | --- |
| Sharky 775 | qp 1.0/1.5 | DN15 | 1.0 | 40 | Ultrasonic |
| Kamstrup 403 | qp 1.5 | DN15 | 1.0 | 40 | Ultrasonic |
| Sontex 749 | qp 1.5 | DN15 | 1.0 | 90 | Oscillation |
| Sontex 449 | qp 1.5 | DN15 | 1.0 | 90 | Oscillation |
| Danfoss SonoSelect 10 | qp 1.5 | DN15 | 1.0 | 70 | Ultrasonic |
| Ista Ultego III Smart plus | qp 1.5 | DN20 | 1.0 | 70 | Ultrasonic |
| Sharky 775 | qp 0.6 | DN15 | 1.0 | 250 | Ultrasonic |
| Kamstrup 403 | qp 0.6 | DN15 | 1.0 | 80 | Ultrasonic |
| Sontex 749 | qp 0.6 | DN15 | 1.0 | 500 | Oscillation |
| Danfoss SonoSelect 10 | qp 0.6 | DN15 | 1.0 | 85 | Ultrasonic |
| Ista Ultego III Smart plus | qp 0.6 | DN20 | 1.0 | 400 | Ultrasonic |

(1 kPa = 10 mbar = 0.01 bar)

Typically heat meters with Qp 1.5 within HIU units, heat meters with Qp 0.6 are shown for comparison.

- Sharky 775

- Kamstrup 403

- Sontex Superstatic 749

- Sontex Superstatic 449

- Danfoss Sonoselect 10

- Ista Ultego III Smart Heat Meter

# Consideration 2

British Standards: BS EN 1434-4, Table B.1 – Checklist for type approvals of heat meters according to EN 1434:

6.1.5. The Maximum pressure loss at Qp shall not exceed 0.25 bar (250mbar/25kPa), except where the heat meter includes a flow controller or also acts as a pressure reducing valve.

# Recommendation

For a typical domestic heat meter with Qp 1.5 the pressure loss at 1.0 m3/h is significantly lower than the restrictor pressure loss 25 kPa currently used in the test.

The recommendation is:

- To reduce the pressure loss to 10 kPa (100 mbar) for the restrictor to simulate a typical heat meter.

- HIU units are proposed to be tested with the restrictor installed to replace the meter.

- The manufacturer can select an option to test with their preferred heat meter. The pressure loss of the meter “X” kPa at 1.0 m3/h should be stated in the components list.

If a HIU is tested with a specific heat meter (option 3 above), the test results will only be applicable for any HIU using a heat meter with the same pressure loss as the installed heat meter or an equivalent heat meter with the same or lower pressure loss when measured at 1.0 m3/h. An HIU that was supplied with a heat meter with a great pressure loss across the heat meter would need to be retested in order to be BESA certified.

# References

[1] Sharky 775 Data Sheet

[2] Kamstrup 403 Data Sheet

[3] Sontex Superstatic 749 and 449 Data Sheet

[4] Danfoss SonoSelect 10 Data Sheet

[5] Ista Ultego III Smart plus Data Sheet

[6] BS EN 1434-4:2015, Heat Meters