## OLD TESTs (hidden)
OLD v2 TESTS
Table 2: Tests to be carried out where both High and Low Temp (60°C & 70°C) primary flows tested
| Test | Description
| 0 | Pressure tests
| 1a | Space Heating 1 kW, 60/40°C secondary
| 1b | Space Heating 2 kW, 60/40°C secondary
| 1c | Space Heating 4 kW, 60/40°C secondary
| 1d | Space Heating 1kW, 45/35°C secondary
| 1e | Space Heating 2kW, 45/35°C secondary
| 1f | Space Heating 4kW, 45/35°C secondary
| 2a | DHW only, DH 70°C flow; 55°C DHW
| 2b | DHW only, DH 60°C flow; 50°C DHW
| 3a | Low flow DHW, DH 70°C flow; 55°C DHW
| 3b | Low flow DHW, DH 60°C flow; 50°C DHW
| 4a | Keep-warm, DH 70°C flow; 55°C DHW
| 4b | Keep-warm, DH 60°C flow; 50°C DHW
| 5a | DHW response time, DH 70°C flow; 55°C DHW
| 5b | DHW response time, DH 60°C flow; 50°C DHW
Table 3: Tests to be carried out where only High Temperature (70°C) primary flows tested
| Test | Description
| 0 | Pressure tests
| 1a | Space Heating 1 kW, 60/40°C secondary
| 1b | Space Heating 2 kW, 60/40°C secondary
| 1c | Space Heating 4 kW, 60/40°C secondary
| 2a | DHW only, DH 70°C flow; 55°C DHW
| 3a | Low flow DHW, DH 70°C flow; 55°C DHW
| 4a | Keep-warm, DH 70°C flow; 55°C DHW
| 5a | DHW response time, DH 70°C flow; 55°C DHW
Table 4: Tests to be carried out where only Low Temperature (60°C) primary flows tested
| Test | Description
| 0 | Pressure tests
| 1d | Space Heating 1kW, 45/35°C secondary
| 1e | Space Heating 2kW, 45/35°C secondary
| 1f | Space Heating 4kW, 45/35°C secondary
| 2b | DHW only, DH 60°C flow; 50°C DHW
| 3b | Low flow DHW, DH 60°C flow; 50°C DHW
| 4b | keep-warm, DH 60°C flow; 50°C DHW
| 5b | DHW response time, DH 60°C flow; 50°C DHW

## OLD TEST categorisation (hidden)
OLD v2 TESTS |  |  | DH ONLY 70C |  | DH ONLY 60C
Test | Description | Test | Description | Test | Description
0 | Pressure tests | 0 | Pressure tests | 0 | Pressure tests
1a | DH/70C, Space Heating 1 kW, 60/40°C secondary | 1a | DH/70C, Space Heating 1 kW, 60/40°C secondary
1b | DH/70C, Space Heating 2 kW, 60/40°C secondary | 1b | Space Heating 2 kW, 60/40°C secondary
1c | DH/70C, Space Heating 4 kW, 60/40°C secondary | 1c | Space Heating 4 kW, 60/40°C secondary
1d | DH/60C, Space Heating 1kW, 45/35°C secondary |  |  | 1d | Space Heating 1kW, 45/35°C secondary
1e | DH/60C, Space Heating 2kW, 45/35°C secondary |  |  | 1e | Space Heating 2kW, 45/35°C secondary
1f | DH/60C, Space Heating 4kW, 45/35°C secondary |  |  | 1f | Space Heating 4kW, 45/35°C secondary
2a | DH/70C, DHW only, 55°C DHW | 2a | DHW only, DH 70°C flow; 55°C DHW
2b | DH/60C, DHW only, 50°C DHW |  |  | 2b | DHW only, DH 60°C flow; 50°C DHW
3a | DH/70C, Low flow DHW, 55°C DHW | 3a | Low flow DHW, DH 70°C flow; 55°C DHW
3b | DH/60C, Low flow DHW, 50°C DHW |  |  | 3b | Low flow DHW, DH 60°C flow; 50°C DHW
4a | DH/70C, Keep-warm, 55°C DHW | 4a | Keep-warm, DH 70°C flow; 55°C DHW
4b | DH/60C, Keep-warm, 50°C DHW |  |  | 4b | keep-warm, DH 60°C flow; 50°C DHW
5a | DH/70C, Non Keep-warm, 55°C DHW
5b | DH/60C, Non Keep-warm, 50°C DHW
6a | DH/70C, DHW response time, 55°C DHW | 6a | DHW response time, DH 70°C flow; 55°C DHW
6b | DH/60C, DHW response time, 50°C DHW |  |  | 6b | DHW response time, DH 60°C flow; 50°C DHW

## INTRO
BESA HIU RESULTS DATABASE
Created by Phil Jones & Keegan Farrelly
v11
15th July 2024
MODULE MENU
| SPACE HEATING | [5 empty] | DHW
| M1 | M2 | M3 | M4 | M5 | M6 | M7 | M8 | M9 | M10
| 01a | 01d | 02a | 02d | 03a | 03d | 11a | 11b | 11a | 11b
| 01b | 01e | 02b | 02e | 03b | 03e | 12a | 12b | 12a | 12b
| 01c | 01f | 02c | 02f | 03c | 03f | 12c | 12d | 12c | 12d
[7 empty] | 13a | 13b | 13a | 13b
[7 empty] | 21a | 21b | 31a | 31b
[7 empty] | 22a | 22b | 32a | 32b

## M1 Database
MODULE M1 - HM1-DH70C - HEATING MODULE 1-DH70 Indirect | [40 empty] | Note: VWART is calculated across tests 1d-1f
[8 empty] | TEST 01a - DH/70C, Space Heating Indirect 0.5 kW, 55/35°C secondary, 50 kPa | [10 empty] | TEST 01b - DH/70C, Space Heating Indirect 1 kW, 55/35°C secondary, 200 kPa | [10 empty] | TEST 01c - DH/70C, Space Heating Indirect 4 kW, 55/35°C secondary, 50 kPa
Manufacturer | Model | Serial No. | Year of manufacture | HIU TYPE (T1-T7) | Test carried out by | Registration Date | BESA Registration Code | PRIMARY Return Temperature [t11] [°C] | PRIMARY Flow Temperature [t12] [°C] | PRIMARY Flow Rate [q1] [Ls−1] | PRIMARY Differential Pressure [dP1] [kPa] | Airthmetic mean of primary side power recorded [H1] [W] | SECONDARY Return Temperature [t21] [°C] | SECONDARY Flow Temperature [t22] [°C] | SECONDARY Flow Rate [q1] [Ls−1] | Airthmetic mean of space heating power recorded [H2] [W] | SECONDARY Heat Load [H2] [W] | VWART [°C] | PRIMARY Return Temperature [t11] [°C] | PRIMARY Flow Temperature [t12] [°C] | PRIMARY Flow Rate [q1] [Ls−1] | PRIMARY Differential Pressure [Δp1] [kPa] | Airthmetic mean of primary side power recorded [H1] [W] | SECONDARY Return Temperature [t21] [°C] | SECONDARY Flow Temperature [t22] [°C] | SECONDARY Flow Rate [q1] [Ls−1] | SECONDARY Differential Pressure [Δp1] [kPa] | Airthmetic mean of space heating power recorded [H2] [W] | VWART [°C] | PRIMARY Return Temperature [t11] [°C] | PRIMARY Flow Temperature [t12] [°C] | PRIMARY Flow Rate [q1] [Ls−1] | PRIMARY Differential Pressure [Δp1] [kPa] | Airthmetic mean of primary side power recorded [H1] [W] | SECONDARY Return Temperature [t21] [°C] | SECONDARY Flow Temperature [t22] [°C] | SECONDARY Flow Rate [q1] [Ls−1] | SECONDARY Differential Pressure [Δp1] [kPa] | Airthmetic mean of space heating power recorded [H2] [W] | VWART [°C] | VWART [°C] Across tests 1a-1c | BEST PRACTICE VWART <37C (YES/NO)
Intatec | HIPER2 | INC239010001AR | 2023 | HI/HWI | Enertek | 2024-05-29 | 001/INTATEC/HIPER2/HIHWI/1278/290524 | 69.7 | 43.6 | 0.0057 | 50.1 | 627 | 35.3 | 54.5 | 0.0061 | 1.23 | 475 | 44 | 70.1 | 40.9 | 0.0126 | 199.4 | 1548 | 35.3 | 54.5 | 0.0129 | 0.92 | 1021 | 41 | 69.8 | 37.6 | 0.0309 | 50.3 | 4165 | 34.9 | 54.6 | 0.0486 | 0.42 | 4037 | 38 | 40 | NO
YGHP | Indirect V2 | 202329065 | 2023 | HI/HWI | Enertek | 2024-06-13 | 003/ YGHP/INDIRECTV2/HIHWI/1278/130624 | 70.4 | 38.1 | 0.0053 | 53 | 715.59 | 35.5 | 54.7 | 0.0061 | 0.1 | 480.67 | 38 | 69.7 | 38.3 | 0.0094 | 201 | 1231.66 | 34.8 | 55.5 | 0.011 | 0.5 | 984.34 | 38 | 69.8 | 38.6 | 0.031 | 51 | 4089.97 | 35.3 | 54.7 | 0.048 | 2 | 3952.51 | 39 | 37 | NO
Cetetherm | Pioneer | 73949023352001 | 2023 | HI/HWI | Enertek | 2024-07-03 | 004/CETETHERM/PIONEER/HIHWI/1278/030724 | 70 | 35.3 | 0.0052 | 50 | 752 | 34.6 | 55.1 | 0.0063 | 24 | 524 | 35 | 69.6 | 35.6 | 0.0089 | 201 | 1272 | 34.8 | 54.6 | 0.014 | 24 | 1109 | 36 | 70.5 | 36.2 | 0.03 | 51 | 4269 | 34.8 | 54.6 | 0.05 | 26 | 4142 | 36 | 36 | YES
Baxi | HI / HWI – 4/50 | F0500240000372 | 2024 | HI/HWI | Enertek | 2024-07-17 | 008/BAXI/HIHWI450/1278/170724 | 70 | 36 | 0.0037 | 54 | 527.52 | 35.4 | 54.6 | 0.0064 | 12 | 479.21 | 36 | 70 | 35.4 | 0.016 | 201 | 2260.15 | 35.4 | 55.1 | 0.013 | 13 | 974.78 | 35 | 69.8 | 35.9 | 0.029 | 55 | 4041.42 | 35 | 54.7 | 0.049 | 22 | 4027.82 | 36 | 36 | YES
Baxi | HI / HWI - 14/50 | F0500240000501 | 2024 | HI/HWI | Enertek | 2024-07-17 | 009/BAXI/HIHWI1450/1278/170724 | 69.6 | 35.3 | 0.0042 | 54 | 600.72 | 35 | 55.2 | 0.0061 | 12 | 502.35 | 35 | 69.7 | 35.1 | 0.012 | 202 | 1758.42 | 35 | 55 | 0.013 | 13 | 1042.25 | 35 | 69.6 | 35.3 | 0.028 | 54 | 3990.65 | 35 | 54.8 | 0.048 | 15 | 4003.56 | 35 | 35 | YES
Bosch | Flow 8500 40 H | 5570-379-000001-7735600740 | 2023 | HI/HWI | Enertek | 2024-07-24 | 005/BOSCH/FLOW850040H/HIHWI/1278/240724 | 70 | 36.6 | 0.0048 | 52 | 671 | 34.8 | 55 | 0.056 | 1 | 463.4 | 37 | 69.7 | 36.4 | 0.0082 | 203 | 1146.1 | 35.1 | 54.7 | 0.012 | 0 | 943.8 | 36 | 70.2 | 38 | 0.033 | 51 | 4452.7 | 35 | 54.8 | 0.052 | 2 | 4319.8 | 38 | 37 | NO
Bosch | Flow 8500 50 H | 5570-379-000001-7735600742 | 2023 | HI/HWI | Enertek | 2024-07-24 | 006/BOSCH/FLOW850050H/HIHWI/1278/240724 | 70 | 36.6 | 0.0048 | 52 | 671 | 34.8 | 55 | 0.056 | 1 | 463.4 | 37 | 69.7 | 36.4 | 0.0082 | 203 | 1146.1 | 35.1 | 54.7 | 0.012 | 0 | 943.8 | 36 | 70.2 | 38 | 0.033 | 51 | 4452.7 | 35 | 54.8 | 0.052 | 2 | 4319.8 | 38 | 37 | NO
Bosch | Flow 8500 60 H | 5570-379-000001-7735600744 | 2023 | HI/HWI | Enertek | 2024-07-24 | 007/BOSCH/FLOW850060H/HIHWI/1278/240724 | 70 | 36.6 | 0.0048 | 52 | 671 | 34.8 | 55 | 0.056 | 1 | 463.4 | 37 | 69.7 | 36.4 | 0.0082 | 203 | 1146.1 | 35.1 | 54.7 | 0.012 | 0 | 943.8 | 36 | 70.2 | 38 | 0.033 | 51 | 4452.7 | 35 | 54.8 | 0.052 | 2 | 4319.8 | 38 | 37 | NO
Vital Energi | vTherm°e (Cu) | 140000-000001 | 2024 | HI/HWI | Enertek | 2025-03-06 | 010/VITAL/VTHERM°E(CU)/HIHWI/1278/060325 | 69.8 | 35.2 | 0.0041 | 54 | 600.4 | 35.3 | 55.3 | 0.0065 | 3 | 533.9 | 35 | 69.7 | 35 | 0.011 | 201 | 1578.3 | 35 | 55.4 | 0.012 | 3 | 1065.7 | 35 | 70.3 | 35.4 | 0.028 | 53 | 4026.2 | 35 | 55.5 | 0.047 | 0 | 4076.9 | 35 | 35 | YES

## M2 Database
MODULE M2 - HM2-DH55C - HEATING MODULE 2-DH55 Indirect | [40 empty] | Note: VWART is calculated across tests 1d-1f
[8 empty] | TEST 01d - DH/55C, Space Heating Indirect 0.5 kW, 45/35°C secondary, 50 kPa | [10 empty] | TEST 01e - DH/55C, Space Heating Indirect 1 kW, 45/35°C secondary, 200 kPa | [10 empty] | TEST 01f - DH/55C, Space Heating Indirect 4kW, 45/35°C secondary, 50 kPa
Manufacturer | Model | Serial No. | Year of manufacture | HIU TYPE (T1-T7) | Test carried out by | Registration Date | BESA Registration Code | PRIMARY Return Temperature [t11] [°C] | PRIMARY Flow Temperature [t12] [°C] | PRIMARY Flow Rate [q1] [Ls−1] | PRIMARY Differential Pressure [dP1] [kPa] | Airthmetic mean of primary side power recorded [H1] [W] | SECONDARY Return Temperature [t21] [°C] | SECONDARY Flow Temperature [t22] [°C] | SECONDARY Flow Rate [q1] [Ls−1] | SECONDARY Differential Pressure [dP2] [kPa] | Airthmetic mean of space heating power recorded [H2] [W] | VWART [°C] | PRIMARY Return Temperature [t11] [°C] | PRIMARY Flow Temperature [t12] [°C] | PRIMARY Flow Rate [q1] [Ls−1] | PRIMARY Differential Pressure [Δp1] [kPa] | Airthmetic mean of primary side power recorded [H1] [W] | SECONDARY Return Temperature [t21] [°C] | SECONDARY Flow Temperature [t22] [°C] | SECONDARY Flow Rate [q1] [Ls−1] | SECONDARY Differential Pressure [Δp1] [kPa] | Airthmetic mean of space heating power recorded [H2] [W] | VWART [°C] | PRIMARY Return Temperature [t11] [°C] | PRIMARY Flow Temperature [t12] [°C] | PRIMARY Flow Rate [q1] [Ls−1] | PRIMARY Differential Pressure [Δp1] [kPa] | Airthmetic mean of primary side power recorded [H1] [W] | SECONDARY Return Temperature [t21] [°C] | SECONDARY Flow Temperature [t22] [°C] | SECONDARY Flow Rate [q1] [Ls−1] | SECONDARY Differential Pressure [Δp1] [kPa] | Airthmetic mean of space heating power recorded [H2] [W] | VWART [°C] | VWART [°C] Across tests 1d-1f | BEST PRACTICE VWART <37C (YES/NO)
Intatec | HIPER2 | INC239010001AR | 2023 | HI/HWI | Enertek | 2024-05-29 | 001/INTATEC/HIPER2/HIHWI/1278/290524 | 54.6 | 37.6 | 0.0079 | 50.5 | 561 | 35.3 | 44.6 | 0.0125 | 73.6 | 483 | 38 | 54.7 | 37.2 | 0.0143 | 200.5 | 1053 | 35.4 | 44.7 | 0.0251 | 73.7 | 978 | 37 | 54.7 | 35.8 | 0.0518 | 50.9 | 4024 | 34.6 | 44.8 | 0.0937 | 71 | 4024 | 36 | 37 | YES
Evinox | TP 70/10 A | HTPE2H4423A57 | 2023 | HI/HWI | Enertek | 2024-06-12 | 002/EVINOX/TP7010A/HIHWI/28/120624 | 54.8 | 34.8 | 0.0065 | 51 | 553 | 34.9 | 44.6 | 0.0122 | 1 | 489 | 35 | 55.1 | 35.9 | 0.0145 | 201 | 1111 | 35.3 | 44.6 | 0.0245 | 1 | 961 | 36 | 54.6 | 37.3 | 0.0563 | 50 | 4070 | 34.7 | 44.8 | 0.0927 | 3 | 3949 | 37 | 36 | YES
YGHP | Indirect V2 | 202329065 | 2023 | HI/HWI | Enertek | 2024-06-13 | 003/ YGHP/INDIRECTV2/HIHWI/1278/130624 | 55 | 37.1 | 0.0075 | 58 | 564.86 | 34.6 | 44.9 | 0.012 | 0.3 | 513.67 | 37 | 54.7 | 36 | 0.013 | 205 | 986.26 | 35 | 44.5 | 0.024 | 2 | 943.62 | 36 | 54.8 | 37.4 | 0.055 | 52 | 4043.4 | 35.5 | 44.7 | 0.102 | 5 | 3965.22 | 37 | 37 | YES
Cetetherm | Pioneer | 73949023352001 | 2023 | HI/HWI | Enertek | 2024-07-03 | 004/CETETHERM/PIONEER/HIHWI/1278/030724 | 54.8 | 34.6 | 0.0081 | 51 | 683 | 34.9 | 45 | 0.013 | 25 | 530 | 35 | 54.5 | 36 | 0.015 | 201 | 1152 | 35.4 | 45.3 | 0.024 | 26 | 970 | 36 | 54.8 | 36.6 | 0.055 | 50 | 4222 | 35.5 | 45.3 | 0.1 | 28 | 4132 | 37 | 36 | YES
Baxi | HI / HWI – 4/50 | F0500240000372 | 2024 | HI/HWI | Enertek | 2024-07-17 | 008/BAXI/HIHWI450/1278/170724 | 55.1 | 35 | 0.006 | 54.51 | 505.86 | 35.2 | 45.1 | 0.012 | 9.03 | 448.06 | 35 | 55.3 | 35.2 | 0.016 | 202.67 | 1380.66 | 35.3 | 44.6 | 0.024 | 11.05 | 949.02 | 35 | 54.5 | 36 | 0.05 | 53.14 | 3818.76 | 35.2 | 44.6 | 0.098 | 38.88 | 3872.52 | 36 | 35 | YES
Baxi | HI / HWI - 14/50 | F0500240000501 | 2024 | HI/HWI | Enertek | 2024-07-17 | 009/BAXI/HIHWI1450/1278/170724 | 54.9 | 34.5 | 0.0069 | 54.61 | 588.81 | 34.6 | 44.7 | 0.012 | 8.19 | 536.05 | 35 | 55.2 | 34.5 | 0.019 | 202.05 | 1638.62 | 34.6 | 45.1 | 0.025 | 8.92 | 1083.66 | 35 | 55.3 | 35.5 | 0.045 | 55.12 | 3759.27 | 35.3 | 44.7 | 0.097 | 18.28 | 3834.41 | 36 | 35 | YES
Bosch | Flow 8500 40 H | 5570-379-000001-7735600740 | 2023 | HI/HWI | Enertek | 2024-07-24 | 005/BOSCH/FLOW850040H/HIHWI/1278/240724 | 54.6 | 35.2 | 0.0071 | 57 | 573.5 | 35.4 | 44.7 | 0.012 | 2 | 464.3 | 35 | 55 | 35.8 | 0.013 | 203 | 1029.8 | 35.4 | 45 | 0.023 | 1 | 940.8 | 36 | 55.3 | 36.7 | 0.05 | 51 | 3824.6 | 35.2 | 44.6 | 0.097 | 6 | 3864.2 | 37 | 36 | YES
Bosch | Flow 8500 50 H | 5570-379-000001-7735600742 | 2023 | HI/HWI | Enertek | 2024-07-24 | 006/BOSCH/FLOW850050H/HIHWI/1278/240724 | 54.6 | 35.2 | 0.0071 | 57 | 573.5 | 35.4 | 44.7 | 0.012 | 2 | 464.3 | 35 | 55 | 35.8 | 0.013 | 203 | 1029.8 | 35.4 | 45 | 0.023 | 1 | 940.8 | 36 | 55.3 | 36.7 | 0.05 | 51 | 3824.6 | 35.2 | 44.6 | 0.097 | 6 | 3864.2 | 37 | 36 | YES
Bosch | Flow 8500 60 H | 5570-379-000001-7735600744 | 2023 | HI/HWI | Enertek | 2024-07-24 | 007/BOSCH/FLOW850060H/HIHWI/1278/240724 | 54.6 | 35.2 | 0.0071 | 57 | 573.5 | 35.4 | 44.7 | 0.012 | 2 | 464.3 | 35 | 55 | 35.8 | 0.013 | 203 | 1029.8 | 35.4 | 45 | 0.023 | 1 | 940.8 | 36 | 55.3 | 36.7 | 0.049 | 51 | 3824.6 | 35.2 | 44.6 | 0.097 | 6 | 3864.2 | 37 | 36 | YES
Vital Energi | vTherm°e (Cu) | 140000-000001 | 2024 | HI/HWI | Enertek | 2025-03-06 | 010/VITAL/VTHERM°E(CU)/HIHWI/1278/060325 | 55.3 | 34.8 | 0.0064 | 54 | 568 | 35.1 | 45.4 | 0.012 | 3 | 529 | 35 | 55.2 | 34.5 | 0.013 | 203 | 1124.5 | 34.5 | 45.4 | 0.024 | 3 | 1106.6 | 34 | 54.8 | 34.9 | 0.049 | 55 | 4270.8 | 34.6 | 45.3 | 0.097 | 3 | 4350.1 | 35 | 35 | YES

## M7 Database
MODULE M7 - DHWM7-DH70C-Kwarm - HOT WATER MODULE 7-DH70-Kwarm
[8 empty] | Test 11a - DH/70C, DHW only, 50°C DHW, variable dP | [6 empty] | Test 12a - DH/70C, DHW Low Flow, 50°C DHW, 50kPa |  |  |  | Test 12c - DH/70C, DHW Low Flow, 50°C DHW, 200kPa |  |  |  | Test 13a - DH/70C, DHW load test, 50°C DHW | [10 empty] | Test 21a - DH/70C, DHW Keep Warm, 50°C DHW | [7 empty] | Test 22a - DH/70C, DHW Keep Warm response time, 50°C DHW
Manufacturer | Model | Serial No. | Year of manufacture | HIU TYPE (T1-T7) | Test carried out by | Registration Date | BESA Registration Code | DHW Minimum temperature [t32] [°C] | DHW Maximum temperature [t32] [°C] | Number of consecutive seconds where t32 > 55°C | Reported VWART (°C) | BEST PRACTICE VWART <17°C (YES/NO) | BEST PRACTICE t32 maintained at 50°C±2°C (YES/NO) | BEST PRACTICE t32 doesn't drop below 45°C for >2 consecutive seconds (YES/NO) | DHW Minimum temperature [t32] [°C] | DHW Maximum temperature [t32] [°C] | Number of consecutive seconds where t32 > 55°C | BEST PRACTICE t32 maintained at 50°C±2°C (YES/NO) | DHW Minimum temperature [t32] [°C] | DHW Maximum temperature [t32] [°C] | Number of consecutive seconds where t32 > 55°C | BEST PRACTICE t32 maintained at 50°C±2°C (YES/NO) | Maximum heat output of test [kW] | Maximum flowrate of test [Ls-1] | PRIMARY Return Temperature [t11] [°C] | PRIMARY Flow Temperature [t12] [°C] | PRIMARY Flow Rate [q1] [Ls−1] | Airthmetic mean of primary side power recorded [H1] [kW] | Cold Water Supply Temperature [t31] [°C] | Domestic hot water flow Temperature [t32] [°C] | Domestic hot water Flow Rate [q3] [Ls−1] | Domestic hot water across HIU Differential Pressure [Δp3] [kPa] | Airthmetic mean of DHW power recorded [H3] [kW] | PRIMARY Flow Rate [q1] [Ls−1] | Mean average of Primary side power [H1] [kW] | Mean average electrical energy use [W electrical] [W] | Mean average thermal energy use [W thermal] [W] | Overall energy loss per day [kWh] | VWART [°C] | BEST PRACTICE VWART <38C (YES/NO) | BEST PRACTICE overall energy losses <0.7 kWh/day (YES/NO) | Time taken for t32 to drop below 42.0°C [s] | Number of consecutive seconds where t32 > 55°C [s] | Mean average volume flow, primary side [q1] [Ls-1] | BEST PRACTICE DHW response time, t32, <10 seconds (YES/NO)
Intatec | HIPER2 | INC239010001AR | 2023 | HI/HWI | Enertek | 2024-05-29 | 001/INTATEC/HIPER2/HIHWI/1278/290524 | 41.1 | 54.7 | 0 | 13 | YES | NO | NO | 51.6 | 57.7 | 18 | NO | 49 | 58.8 | 13 | NO | 70 | 0.42 | 69.5 | 15.6 | 0.29 | 66 | 9.8 | 47.3 | 0.42 | 148 | 66.5 | 0.0009 | 0.04 | 1.45 | 36.4 | 0.91 | 38 | NO | NO | 10 | 0 | 0.129 | NO
YGHP | Indirect V2 | 202329065 | 2023 | HI/HWI | Enertek | 2024-06-13 | 003/ YGHP/INDIRECTV2/HIHWI/1278/130624 | 42.9 | 52.8 | 0 | 14 | YES | NO | NO | 48.5 | 58.7 | 48 | NO | 51 | 55 | 2 | NO | 65 | 0.39 | 70.3 | 15.4 | 0.244 | 55.04 | 9.7 | 43.3 | 0.391 | 144 | 55.03 | 0.0008 | 0.03 | 1.82 | 32.4 | 0.82 | 37 | YES | NO | 14 | 0 | 0.115 | NO
Cetetherm | Pioneer | 73949023352001 | 2023 | HI/HWI | Enertek | 2024-07-03 | 004/CETETHERM/PIONEER/HIHWI/1278/030724 | 46.8 | 56.9 | 17 | 15 | YES | NO | YES | 49.2 | 52.9 | 0 | NO | 49.5 | 52.3 | 0 | NO | 70 | 0.42 | 69.7 | 20.6 | 0.334 | 52.57 | 10.1 | 48.2 | 0.424 | 1.4 | 67.58 | 0.0008 | 0.037 | 3 | 36.7 | 0.95 | 33 | YES | NO | 15 | 0 | 0.118 | NO
Baxi | HI / HWI – 4/50 | F0500240000372 | 2024 | HI/HWI | Enertek | 2024-07-17 | 008/BAXI/HIHWI450/1278/170724 | 45 | 54.5 | 0 | 12 | YES | NO | YES | 36.6 | 54.8 | 0 | NO | 37.9 | 54.1 | 0 | NO | 70 | 0.42 | 70.3 | 15.1 | 0.297 | 68.49 | 10 | 49.8 | 0.42 | 94 | 70.02 | 0.0009 | 0.04 | 3 | 36.7 | 0.952 | 39 | NO | NO | 10 | 0 | 0.087 | NO
Baxi | HI / HWI - 14/50 | F0500240000501 | 2024 | HI/HWI | Enertek | 2024-07-17 | 009/BAXI/HIHWI1450/1278/170724 | 45 | 54.5 | 0 | 12 | YES | NO | YES | 36.6 | 54.8 | 0 | NO | 37.9 | 54.1 | 0 | NO | 70 | 0.42 | 70.3 | 15.1 | 0.297 | 68.49 | 10 | 49.8 | 0.42 | 94 | 70.02 | 0.0009 | 0.04 | 3 | 36.7 | 0.952 | 39 | NO | NO | 10 | 0 | 0.087 | NO
Bosch | Flow 8500 40 H | 5570-379-000001-7735600740 | 2023 | HI/HWI | Enertek | 2024-07-24 | 005/BOSCH/FLOW850040H/HIHWI/1278/240724 | 39.7 | 55.5 | 4 | 14 | YES | NO | NO | 47.3 | 53.9 | 0 | NO | 46.6 | 53.9 | 0 | NO | 55 | 0.33 | 70.3 | 15.3 | 0.211 | 48.6 | 9.9 | 50.4 | 0.291 | 219 | 49.6 | 0.0009 | 0.03 | 2.6 | 32 | 0.831 | 39 | NO | NO | 11 | 0 | 0.11 | NO
Bosch | Flow 8500 50 H | 5570-379-000001-7735600742 | 2023 | HI/HWI | Enertek | 2024-07-24 | 006/BOSCH/FLOW850050H/HIHWI/1278/240724 | 40 | 56.9 | 10 | 14 | YES | NO | NO | 47.6 | 56.9 | 21 | NO | 47.9 | 56.9 | 23 | NO | 65 | 0.39 | 70.3 | 14.9 | 0.252 | 58.3 | 9.8 | 47.8 | 0.374 | 180 | 59.4 | 0.0007 | 0.03 | 2.5 | 26.3 | 0.692 | 39 | NO | YES | 12 | 0 | 0.107 | NO
Bosch | Flow 8500 60 H | 5570-379-000001-7735600744 | 2023 | HI/HWI | Enertek | 2024-07-24 | 007/BOSCH/FLOW850060H/HIHWI/1278/240724 | 38.5 | 57 | 10 | 14 | YES | NO | NO | 48.3 | 56.1 | 12 | NO | 48.4 | 56.2 | 16 | NO | 70 | 0.42 | 69.5 | 15.3 | 0.271 | 61.6 | 10 | 49 | 0.424 | 176 | 62.1 | 0.0009 | 0.03 | 2.6 | 33.3 | 0.86 | 39 | NO | NO | 9 | 0 | 0.111 | YES
Vital Energi | vTherm°e (Cu) | 140000-000001 | 2024 | HI/HWI | Enertek | 2025-03-06 | 010/VITAL/VTHERM°E(CU)/HIHWI/1278/060325 | 41.7 | 55 | 1 | 14 | YES | NO | NO | 48.8 | 55.8 | 6 | NO | 40.1 | 56.8 | 10 | NO | 70 | 0.42 | 70.4 | 17.1 | 0.319 | 71.1 | 9.8 | 51.4 | 0.42 | 79 | 73.1 | 0.0006 | 0.03 | 2.8 | 26.4 | 0.696 | 33 | YES | YES | 15 | 0 | 0.111 | NO

## M8 Database
MODULE M8 - DHWM8-DH55C-Kwarm - HOT WATER MODULE 8-DH55-Kwarm
[8 empty] | Test 11b - DH/55C, DHW only, 50°C DHW, variable dP | [6 empty] | Test 12b - DH/55C, DHW Low flow, 50°C DHW, 50kPa |  |  |  | Test 12d - DH/55C, DHW Low flow, 50°C DHW, 200kPa |  |  |  | Test 13b - DH/55C, DHW load test, 50°C DHW | [10 empty] | Test 21b - DH/55C, DHW Keep Warm, 50°C DHW | [7 empty] | Test 22b - DH/55C, DHW Keep Warm response time, 50°C DHW
Manufacturer | Model | Serial No. | Year of manufacture | HIU TYPE (T1-T7) | Test carried out by | Registration Date | BESA Registration Code | DHW Minimum temperature [t32] [°C] | DHW Maximum temperature [t32] [°C] | Number of consecutive seconds where t32 > 55°C | Reported VWART (°C) | BEST PRACTICE VWART <20°C (YES/NO) | BEST PRACTICE t32 maintained at 50°C±2°C (YES/NO) | BEST PRACTICE t32 doesn't drop below 45°C for >2 consecutive seconds (YES/NO) | DHW Minimum temperature [t32] [°C] | DHW Maximum temperature [t32] [°C] | Number of consecutive seconds where t32 > 55°C | BEST PRACTICE t32 maintained at 50°C±2°C (YES/NO) | DHW Minimum temperature [t32] [°C] | DHW Maximum temperature [t32] [°C] | Number of consecutive seconds where t32 > 55°C | BEST PRACTICE t32 maintained at 50°C±2°C (YES/NO) | Maximum heat output of test [kW] | Maximum flowrate of test [Ls-1] | PRIMARY Return Temperature [t11] [°C] | PRIMARY Flow Temperature [t12] [°C] | PRIMARY Flow Rate [q1] [Ls−1] | Airthmetic mean of primary side power recorded [H1] [kW] | Cold Water Supply Temperature [t31] [°C] | Domestic hot water flow Temperature [t32] [°C] | Domestic hot water Flow Rate [q3] [Ls−1] | Domestic hot water across HIU Differential Pressure [Δp3] [kPa] | Airthmetic mean of DHW power recorded [H3] [kW] | PRIMARY Flow Rate [q1] [Ls−1] | Mean average of Primary side power [H1] [kW] | Mean average electrical energy use [W electrical] [W] | Mean average thermal energy use [W thermal] [W] | Overall energy loss per day [kWh] | VWART [°C] | BEST PRACTICE VWART <44°C (YES/NO) | BEST PRACTICE overall energy losses <0.7 kWh/day (YES/NO) | Time taken for t32 to reach 45.0°C and not drop below 42.0°C [s] | Number of consecutive seconds where t32 > 55°C [s] | Mean average volume flow, primary side [q1] [Ls-1] | BEST PRACTICE DHW response time, t32, <10 seconds (YES/NO)
Intatec | HIPER2 | INC239010001AR | 2023 | HI/HWI | Enertek | 2024-05-29 | 001/INTATEC/HIPER2/HIHWI/1278/290524 | 44.9 | 53.5 | 0 | 20 | NO | NO | YES | 48.2 | 52.9 | 0 | NO | 47.2 | 52.6 | 0 | NO | 55 | 0.33 | 55.2 | 16.8 | 0.29 | 46.7 | 9.8 | 43.7 | 0.33 | 92 | 47 | 0.0016 | 0.107 | 0.58 | 33.7 | 0.82 | 39 | YES | NO | 11 | 0 | 0.168 | NO
Evinox | TP 70/10 A | HTPE2H4423A57 | 2023 | HI/HWI | Enertek | 2024-06-12 | 002/EVINOX/TP7010A/HIHWI/28/120624 | 44.1 | 53.5 | 0 | 16 | YES | NO | NO | 36.2 | 52.8 | 0 | NO | 36.1 | 52.5 | 0 | NO | 60 | 0.36 | 54.7 | 15 | 0.314 | 51.6 | 9.7 | 44 | 0.361 | 73 | 51.9 | 0.0016 | 0.03 | 5.2 | 31.1 | 0.87 | 45 | NO | NO | 7 | 0 | 0.121 | YES
YGHP | Indirect V2 | 202329065 | 2023 | HI/HWI | Enertek | 2024-06-13 | 003/ YGHP/INDIRECTV2/HIHWI/1278/130624 | 46.9 | 52.7 | 0 | 21.5 | NO | NO | NO | 49 | 52.3 | 0 | NO | 50.4 | 53 | 0 | NO | 45 | 0.27 | 54.9 | 19.9 | 0.27 | 39.53 | 9.9 | 44.8 | 0.27 | 73 | 39.52 | 0.0014 | 0.03 | 1.85 | 19.3 | 0.51 | 41 | YES | YES | 15 | 0 | 0.165 | NO
Cetetherm | Pioneer | 73949023352001 | 2023 | HI/HWI | Enertek | 2024-07-03 | 004/CETETHERM/PIONEER/HIHWI/1278/030724 | 46.1 | 53.7 | 0 | 23 | NO | NO | YES | 49.4 | 50.2 | 0 | NO | 49 | 50.1 | 0 | NO | 55 | 0.33 | 54.7 | 22.5 | 0.35 | 47.23 | 10.1 | 44.1 | 0.33 | 89 | 47.13 | 0.0014 | 0.04 | 3.1 | 37.6 | 0.975 | 37 | YES | NO | 15 | 0 | 0.163 | NO
Baxi | HI / HWI – 4/50 | F0500240000372 | 2024 | HI/HWI | Enertek | 2024-07-17 | 008/BAXI/HIHWI450/1278/170724 | 47.8 | 52.9 | 0 | 18 | YES | NO | YES | 32.7 | 52.7 | 0 | NO | 45.9 | 52 | 0 | NO | 60 | 0.36 | 55.3 | 15.6 | 0.297 | 49.28 | 9.8 | 43.3 | 0.36 | 71 | 50.47 | 0.0015 | 0.03 | 3 | 34.9 | 0.91 | 39 | YES | NO | 14 | 0 | 0.116 | NO
Baxi | HI / HWI - 14/50 | F0500240000501 | 2024 | HI/HWI | Enertek | 2024-07-17 | 009/BAXI/HIHWI1450/1278/170724 | 47.8 | 52.9 | 0 | 18 | YES | NO | YES | 32.7 | 52.7 | 0 | NO | 45.9 | 52 | 0 | NO | 60 | 0.36 | 55.3 | 15.6 | 0.297 | 49.28 | 9.8 | 43.3 | 0.36 | 71 | 50.47 | 0.0015 | 0.03 | 3 | 34.9 | 0.91 | 39 | YES | NO | 14 | 0 | 0.116 | NO
Bosch | Flow 8500 40 H | 5570-379-000001-7735600740 | 2023 | HI/HWI | Enertek | 2024-07-24 | 005/BOSCH/FLOW850040H/HIHWI/1278/240724 | 45.5 | 52.4 | 0 | 20 | NO | NO | YES | 47.4 | 51 | 0 | NO | 46.5 | 51.7 | 0 | NO | 50 | 0.3 | 55.4 | 16.9 | 0.263 | 42.8 | 9.8 | 44.4 | 0.301 | 127 | 43.6 | 0.0019 | 0.03 | 2.6 | 35.5 | 0.913 | 42 | YES | NO | 11 | 0 | 0.169 | NO
Bosch | Flow 8500 50 H | 5570-379-000001-7735600742 | 2023 | HI/HWI | Enertek | 2024-07-24 | 006/BOSCH/FLOW850050H/HIHWI/1278/240724 | 45.6 | 52.4 | 0 | 21 | NO | YES | YES | 48.9 | 51.6 | 0 | YES | 49.3 | 51.9 | 0 | YES | 50 | 0.3 | 53.9 | 16.6 | 0.265 | 41.3 | 9.7 | 43.1 | 0.3 | 102 | 42 | 0.0017 | 0.03 | 2.5 | 30.5 | 0.795 | 42 | YES | NO | 12 | 0 | 0.161 | NO
Bosch | Flow 8500 60 H | 5570-379-000001-7735600744 | 2023 | HI/HWI | Enertek | 2024-07-24 | 007/BOSCH/FLOW850060H/HIHWI/1278/240724 | 45.5 | 52.3 | 0 | 20 | NO | NO | YES | 48.7 | 51.8 | 0 | YES | 48.8 | 51.8 | 0 | YES | 55 | 0.33 | 55.2 | 15.9 | 0.274 | 45.1 | 9.9 | 43 | 0.33 | 123 | 45.7 | 0.002 | 0.04 | 2.6 | 40.1 | 0.997 | 41 | YES | NO | 11 | 0 | 0.168 | NO
Vital Energi | vTherm°e (Cu) | 140000-000001 | 2024 | HI/HWI | Enertek | 2025-03-06 | 010/VITAL/VTHERM°E(CU)/HIHWI/1278/060325 | 44.8 | 52.5 | 0 | 20 | YES | NO | NO | 48.9 | 52.4 | 0 | NO | 49.1 | 52.6 | 0 | NO | 60 | 0.36 | 55.4 | 16.9 | 0.3124 | 50.2 | 9.5 | 43.8 | 0.36 | 61 | 51.8 | 0.0014 | 0.04 | 2.8 | 38.3 | 0.987 | 38 | YES | NO | 14 | 0 | 0.133 | NO

## OLD Database (hidden)
|  | MODULE M1 |  |  | MODULE M2 |  |  | MODULE M3 |  |  | MODULE M4 |  |  | MODULE M5 |  |  | MODULE M6 |  |  | MODULE M7 | [5 empty] | MODULE M8 | [5 empty] | MODULE M9 | [5 empty] | MODULE M10
MODULE CODE | MODULES | HM1-DH70C - HEATING MODULE 1-DH70 Indirect |  |  | HM2-DH55C - HEATING MODULE 2-DH55 Indirect |  |  | HM3-DH70C - HEATING MODULE 3-DH70 Direct No Mix Down |  |  | HM4-DH55C - HEATING MODULE 4-DH55 Direct No Mix Down |  |  | HM5-DH70C - HEATING MODULE 5-DH70 Direct Inc Mix Down |  |  | HM6-DH55C - HEATING MODULE 6-DH55 Direct Inc Mix Down |  |  | DHWM7-DH70C-Kwarm - HOT WATER MODULE 7-DH70-KWarm | [5 empty] | DHWM8-DH55C-Kwarm - HOT WATER MODULE 8-DH55-KWarm | [5 empty] | DHWM9-DH70C-Non Kwarm - HOT WATER MODULE 9-DH70-Non KWarm | [5 empty] | DHWM10-DH55C-Non Kwarm - HOT WATER MODULE 10-DH55-Non KWarm
|  | 01a | 01b | 01c | 01d | 01e | 01f | 02a | 02b | 02c | 02d | 02e | 02f | 03a | 03b | 03c | 03d | 03e | 03f | 11a | 12a | 12c | 13a | 21a | 22a | 11b | 12b | 12d | 13b | 21b | 22b | 11a | 12a | 12c | 13a | 31a | 32a | 11b | 12b | 12d | 13b | 31b | 32b
01a | DH/70C, Space Heating Indirect 0.5 kW, 55/35°C secondary, 50 kPa | DH/70C, Space Heating Indirect 0.5 kW, 55/35°C secondary, 50 kPa | DH/70C, Space Heating Indirect 1 kW, 55/35°C secondary, 200 kPa | DH/70C, Space Heating Indirect 4 kW, 55/35°C secondary, 50 kPa | DH/55C, Space Heating Indirect 0.5 kW, 45/35°C secondary, 50 kPa | DH/55C, Space Heating Indirect 1 kW, 45/35°C secondary, 200 kPa | DH/55C, Space Heating Indirect 4kW, 45/35°C secondary, 50 kPa | DH/70C, Space Heating Direct, No Mix Down 0.5 kW, 70/35°C secondary | DH/70C, Space Heating Direct, No Mix Down 1 kW, 70/35°C secondary | DH/70C, Space Heating Direct, No Mix Down 4 kW, 70/35°C secondary | DH/55C, Space Heating Direct, No Mix Down 0.5 kW, 55/35°C secondary | DH/55C, Space Heating Direct, No Mix Down 1 kW, 55/35°C secondary | DH/55C, Space Heating Direct, No Mix Down 4kW, 55/35°C secondary | DH/70C, Space Heating Direct, Inc Mix Down 0.5 kW, 55/35°C secondary | DH/70C, Space Heating Direct, Inc Mix Down 1 kW, 55/35°C secondary | DH/70C, Space Heating Direct, Inc Mix Down 4 kW, 55/35°C secondary | DH/55C, Space Heating Direct, Inc Mix Down 0.5 kW, 45/35°C secondary | DH/55C, Space Heating Direct Test, Inc Mix Down 1 kW, 45/35°C secondary | DH/55C, Space Heating Direct, Inc Mix Down 4kW, 45/35°C secondary | DH/70C, DHW only, 50°C DHW, variable dP | DH/70C, DHW Low flow, 50°C DHW, 50kPa | DH/70C, DHW Low flow, 50°C DHW, 200kPa | DH/70C, DHW load test, 50°C DHW | DH/70C, DHW Keep Warm, 50°C DHW | DH/70C, DHW Keep Warm response time, 50°C DHW | DH/55C, DHW only, 50°C DHW, variable dP | DH/55C, DHW Low flow, 50°C DHW, 50kPa | DH/55C, DHW Low flow, 50°C DHW, 200kPa | DH/55C, DHW load test, 50°C DHW | DH/55C, DHW Keep Warm, 50°C DHW | DH/55C, DHW Keep Warm response time, 50°C DHW | DH/70C, DHW only, 50°C DHW | DH/70C, DHW Low flow, 50°C DHW, 50kPa | DH/70C, DHW Low flow, 50°C DHW, 200kPa | DH/70C, DHW load test, 50°C DHW | DH/70C, DHW Non Keep Warm, 50°C DHW | DH/70C, DHW Non Keep Warm response time, 50°C DHW | DH/55C, DHW only, 50°C DHW | DH/55C, DHW Low flow, 50°C DHW, 50kPa | DH/55C, DHW Low flow, 50°C DHW, 200kPa | DH/55C, DHW load test, 50°C DHW | DH/55C, DHW Non Keep Warm, 50°C DHW | DH/55C, DHW Non Keep Warm response time, 50°C DHW
01b | DH/70C, Space Heating Indirect 1 kW, 55/35°C secondary, 200 kPa
01d | DH/55C, Space Heating Direct, No Mix Down 0.5 kW, 55/35°C secondary
01e | DH/55C, Space Heating Direct, No Mix Down 1 kW, 55/35°C secondary
01f | DH/55C, Space Heating Direct, No Mix Down 4kW, 55/35°C secondary
02a | DH/70C, Space Heating Direct, No Mix Down 0.5 kW, 70/35°C secondary
02b | DH/70C, Space Heating Direct, No Mix Down 1 kW, 70/35°C secondary
02c | DH/70C, Space Heating Direct, No Mix Down 4 kW, 70/35°C secondary
02d | DH/55C, Space Heating Direct, No Mixing Valve 0.5 kW, 45/35°C secondary
02e | DH/55C, Space Heating Direct, No Mixing Valve 1 kW, 45/35°C secondary
02f | DH/55C, Space Heating Direct, No Mixing Valve 4kW, 45/35°C secondary
03a | DH/70C, Space Heating Direct, Inc Mix Down 0.5 kW, 55/35°C secondary
03b | DH/70C, Space Heating Direct, Inc Mix Down 1 kW, 55/35°C secondary
03c | DH/70C, Space Heating Direct, Inc Mix Down 4 kW, 55/35°C secondary
03d | DH/55C, Space Heating Direct, Inc Mix Down 0.5 kW, 45/35°C secondary
03e | DH/55C, Space Heating Direct Test, Inc Mix Down 1 kW, 45/35°C secondary
03f | DH/55C, Space Heating Direct, Inc Mix Down 4kW, 45/35°C secondary
11a | DH/70C, DHW only, 50°C DHW, variable dP
12a | DH/70C, DHW Low flow, 50°C DHW, 50kPa
12c | DH/70C, DHW Low flow, 50°C DHW, 200kPa
13a | DH/70C, DHW load test, 50°C DHW
21a | DH/70C, DHW Keep Warm, 50°C DHW
22a | DH/70C, DHW Keep Warm response time, 50°C DHW
11b | DH/55C, DHW only, 50°C DHW, variable dP
12b | DH/55C, DHW Low flow, 50°C DHW, 50kPa
12d | DH/55C, DHW Low flow, 50°C DHW, 200kPa
13b | DH/55C, DHW load test, 50°C DHW
21b | DH/55C, DHW Keep Warm, 50°C DHW
22b | DH/55C, DHW Keep Warm response time, 50°C DHW
11a | DH/70C, DHW only, 50°C DHW
12a | DH/70C, DHW Low flow, 50°C DHW, 50kPa
12c | DH/70C, DHW Low flow, 50°C DHW, 200kPa
13a | DH/70C, DHW load test, 50°C DHW
31a | DH/70C, DHW Non Keep Warm, 50°C DHW
32a | DH/70C, DHW Non Keep Warm response time, 50°C DHW
11b | DH/55C, DHW only, 50°C DHW
12b | DH/55C, DHW Low flow, 50°C DHW, 50kPa
12d | DH/55C, DHW Low flow, 50°C DHW, 200kPa
13b | DH/55C, DHW load test, 50°C DHW
31b | DH/55C, DHW Non Keep Warm, 50°C DHW
32b | DH/55C, DHW Non Keep Warm response time, 50°C DHW

## OLD Results (hidden)
|  | Power (W) | Primary Flow (m3/hr) | VWART (deg C) | Energy Used (kWh) | Annual operation (hours) | Volume (m3) | Events per year | Average duration (seconds)
DHW Low Flow Rate
DHW Medium Flow Rate
DHW High Flow Rate
DHW Post Low Flow Rate
DHW Post Medium Flow Rate
DHW Post High Flow Rate
| Results |  |  | NEW | OLD | From Enertek report
DHW Only Tests | DHW Min temp |  |  | 11a | 2a | The domestic hot water output temperature, t32 did not exceed 65 °C for more than 10 seconds.
| DHW max temp |  |  |  | 2a | The maximum and minimum temperatures of t32 were 63.4 °C and 46.9 °C respectively.
| DHW output temp not exceed 65C for 10 sec |  |  | 11b | 2b | The domestic hot water output temperature, t32 did not exceed 65 °C for more than 10 seconds.
| VWART |  |  |  | 2b | The maximum and minimum temperatures of t32 were 54.52 °C and 44.01 °C respectively.
Power (W)
DHW Low Flow Tests | DHW Min temp at low flow |  |  | 12a | 3a Lo flo | The domestic hot water output temperature, t32 did not exceed 65 °C for more than 10 seconds.
| DHW Max temp at low flow |  |  |  |  | The appliance did maintain the DHW output temperature, t32 at 55 ± 3 °C during the last 60 seconds of the test.
| Report on the number of consecutive seconds >55°C. |  |  |  |  | The maximum and minimum temperatures of t32 were 58.14 °C and 49.91 °C respectively.
| PASS/FAIL, Fail if t32 not maintained >47C AND <53C for >60seconds (stability) |  |  | 12b | 3b Lo flo | The domestic hot water output temperature, t32 did not exceed 65 °C for more than 10 seconds.
| FAIL: t32 >60C for more than 1 sec (scalding) |  |  |  |  | The appliance did maintain the DHW output temperature, t32 at 55 ± 3 °C during the last 60 seconds of the test.
The maximum and minimum temperatures of t32 were 58.14 °C and 49.91 °C respectively.
(NEW) DHW Load Tests | DHW Min temp at 0.42 l/s
DHW Max temp at 0.42 l/s
Temperature variance around 50.0C
Delivered DHW >45C at the end of the 720 second period with 0.42 l/s,
Pressure drop across HIU at the end of the 720 second period with 0.42 l/s
PASS/FAIL if t12 >55C for more than 5 secs (scaling)
PASS/FAIL if t32 <50C±0.5°C at 0.15 l/s flow rate
DHW Keep Warm Tests | Valid keep Warm function achieved (YES/NO) |  |  | 21a | 4a | The appliance is performing Keep-Warm cycling as the primary flow temperature, t11 varies by more than ± 3 °C during the final 3 hours of the test.
| Average (Standby) primary heat load (W) |  |  |  |  | The average heat load on the primary side 𝑃 is 42 W.
| Average (Standby) Primary Flow (l/hr) |  |  |  |  | The average primary flow 𝑞1 over the 8 hours test was 3.3 l/hr.
| DHW Min temperature (°C) |  |  |  |  | t12 exceeds 50°C at any time
DHW Max temperature (°C)
DHW temperature t12 exceeds 50°C at any time (YES/NO)
Number of consecutive seconds >55°C
Average Standby electrical consumption (W)
Total HIU standby heat loss (W) [DH+electrical]
PASS/FAIL, Fail if HIU heat loss > 1.0kWh/day
PASS/FAIL, Fail if VWART is above 44C
PASS/FAIL, Fail if t11 < 39C (keepwarm)
PASS/FAIL, Fail if t12 >=60C for 1 sec (scalding)
BEST PRACTICE if VWART below 40C
BEST PRACTICE if HIU heat loss less than 0.75 kWh/day"
DHW Response time Tests | Time for DHW temperature t32 to reach 45C |  |  | 22a | 5a | The domestic hot water output temperature, t32 did not exceed 65 °C for more than 10 seconds.
| DHW Min temperature (°C) |  |  |  |  | The DHW response time for 𝑡32 to reach 45 °C (and not subsequently drop below 42 °C) was 13 seconds; therefore this is a valid keep warm.
| DHW Max temperature (°C) |  |  |  |  | Pass/Fail on DHW (at t32) exceeding 60.0°C (to 1 decimal point) for more than 1 second
| Number of consecutive seconds >55°C |  |  |  |  | Report on the number of consecutive seconds >55°C.
| PASS/FAIL if DHW temperature t32 did not exceed 65 °C for > 10 seconds |  |  |  |  | State the maximum and minimum DHW temperatures over the period of the test when there is a DHW flow.
| PASS/FAIL if DHW t32 > 60.0°C for more than 1 second |  |  |  |  | State time to achieve a DHW temperature 45.0°C (1 decimal place) and not subsequently drop below 42.0°C (1 decimal place)
PASS/FAIL if if DHW t32 >15 secs to reach 45C
BEST PRACTICE if DHW t32 <10 secs to reach 45C

## DWH Only (hidden)
|  |  | Power (W) |  |  | Primary Flow (m3/hr) | [5 empty] | VWART (°C) | [5 empty] | Energy Used (kWh) |  |  | Annual operation (hours) |  |  | Volume (m3) | [5 empty] | Events per year |  |  | Average duration (seconds)
DHW output temp not exceed 65°C for 10 sec | DHW Minimum temperature (°C) | DHW Maximum temperature (°C) | POWER (W) [DHW Low Flow Rate] | POWER (W) [DHW Medium Flow Rate] | POWER (W) [DHW High Flow Rate] | Primary Flow (m3/hr) [DHW Low Flow Rate] | Primary Flow (m3/hr) [DHW Medium Flow Rate] | Primary Flow (m3/hr) [DHW High Flow Rate] | Primary Flow (m3/hr) [DHW Post Low Flow Rate] | Primary Flow (m3/hr) [DHW Post Medium Flow Rate] | Primary Flow (m3/hr) [DHW Post High Flow Rate] | VWART (°C) [DHW Low Flow Rate] | VWART (°C) [DHW Medium Flow Rate] | VWART (°C) [DHW High Flow Rate] | VWART (°C) [DHW Post Low Flow Rate] | VWART (°C) [DHW Post Medium Flow Rate] | VWART (°C) [DHW Post High Flow Rate] | Energy Used (kWh) [DHW Low Flow Rate] | Energy Used (kWh) [DHW Medium Flow Rate] | Energy Used (kWh) [DHW High Flow Rate] | Annual operation (hours) [DHW Low Flow Rate] | Annual operation (hours) [DHW Medium Flow Rate] | Annual operation (hours) [DHW High Flow Rate] | Volume (m3) [DHW Low Flow Rate] | Volume (m3) [DHW Medium Flow Rate] | Volume (m3) [DHW High Flow Rate] | Volume (m3) [DHW Post Low Flow Rate] | Volume (m3) [DHW Post Medium Flow Rate] | Volume (m3) [DHW Post High Flow Rate] | Events per year [DHW Post Low Flow Rate] | Events per year [DHW Post Medium Flow Rate] | Events per year [DHW Post High Flow Rate] | Average duration (seconds) [DHW Post Low Flow Rate] | Average duration (seconds) [DHW Post Medium Flow Rate] | Average duration (seconds) [DHW Post High Flow Rate]

## Compare changes (hidden)
OLD |  | NEW
Test | Description | Test | Description
0 | Pressure tests | 00 | Pressure tests
1a | DH/70C, Space Heating 1 kW, 60/40°C secondary | 01a | DH/70C, Space Heating Indirect 0.5 kW, 55/35°C secondary, 50 kPa | Space Htg Indirect
1b | DH/70C, Space Heating 2 kW, 60/40°C secondary | 01b | DH/70C, Space Heating Indirect 1 kW, 55/35°C secondary, 200 kPa
1c | DH/70C, Space Heating 4 kW, 60/40°C secondary | 01c | DH/70C, Space Heating Indirect 4 kW, 55/35°C secondary, 50 kPa
1d | DH/60C, Space Heating 1kW, 45/35°C secondary | 01d | DH/55C, Space Heating Indirect 0.5 kW, 45/35°C secondary, 50 kPa
1e | DH/60C, Space Heating 2kW, 45/35°C secondary | 01e | DH/55C, Space Heating Indirect 1 kW, 45/35°C secondary, 200 kPa
1f | DH/60C, Space Heating 4kW, 45/35°C secondary | 01f | DH/55C, Space Heating Indirect 4kW, 45/35°C secondary, 50 kPa
2a | DH/70C, Space Heating Mixing Valve test | 02a | DH/70C, Space Heating Direct, No Mixing Valve 0.5 kW, 70/35°C secondary | Sp Htg direct No MV
2b | DH/60C, Space Heating Mixing Valve test | 02b | DH/70C, Space Heating Direct, No Mixing Valve 1 kW, 70/35°C secondary
|  | 02c | DH/70C, Space Heating Direct, No Mixing Valve 4 kW, 70/35°C secondary
|  | 02d | DH/55C, Space Heating Direct, No Mixing Valve 0.5 kW, 55/35°C secondary
|  | 02e | DH/55C, Space Heating Direct, No Mixing Valve 1 kW, 55/35°C secondary
|  | 02f | DH/55C, Space Heating Direct, No Mixing Valve 4kW, 55/35°C secondary
|  | 03a | DH/70C, Space Heating Direct, Inc Mixing Valve 0.5 kW, xx/xx°C secondary | Sp Htg Direct Inc MV | More direct space heating modules to be added in the future (e.g. direct with mixing valve within HIU)
|  | 03b | DH/70C, Space Heating Direct, Inc Mixing Valve 1 kW, xx/xx°C secondary
|  | 03c | DH/70C, Space Heating Direct, Inc Mixing Valve 4 kW, xx/xx°C secondary
|  | 03d | DH/55C, Space Heating Direct, Inc Mixing Valve 0.5 kW, xx/xx°C secondary
|  | 03e | DH/55C, Space Heating Direct Test, Inc Mixing Valve 1 kW, xx/xx°C secondary
|  | 03f | DH/55C, Space Heating Direct, Inc Mixing Valve 4kW, xx/xx°C secondary
11a | DH/70C, DHW only, 55°C DHW | 11a | DH/70C, DHW only, 50°C DHW | DHW Only
11b | DH/60C, DHW only, 50°C DHW | 11b | DH/55C, DHW only, 50°C DHW
12a | DH/70C, DHW Low flow, 55°C DHW | 12a | DH/70C, DHW Low flow, 50°C DHW, 50kPa | DHW Low Flow
12b | DH/60C, DHW Low flow, 50°C DHW | 12b | DH/55C, DHW Low flow, 50°C DHW, 50kPa
|  | 12c | DH/70C, DHW Low flow, 50°C DHW, 200kPa
|  | 12d | DH/55C, DHW Low flow, 50°C DHW, 200kPa
13a | DH/70C, DHW load test, 55°C DHW | 13a | DH/70C, DHW load test, 50°C DHW | DHW Load Test
13b | DH/60C, DHW load test, 50°C DHW | 13b | DH/55C, DHW load test, 50°C DHW
21a | DH/70C, DHW Keep Warm, 55°C DHW | 21a | DH/70C, DHW Keep Warm, 50°C DHW | DHW Keep Warm
21b | DH/60C, DHW Keep Warm, 50°C DHW | 21b | DH/55C, DHW Keep Warm, 50°C DHW
22a | DH/70C, DHW Keep Warm response time, 55°C DHW | 22a | DH/70C, DHW Keep Warm response time, 50°C DHW
22b | DH/60C, DHW Keep Warm response time, 50°C DHW | 22b | DH/55C, DHW Keep Warm response time, 50°C DHW
31a | DH/70C, DHW Non Keep Warm, 55°C DHW | 31a | DH/70C, DHW Non Keep Warm, 50°C DHW | DHW Non Keep Warm
31b | DH/60C, DHW Non Keep Warm, 50°C DHW | 31b | DH/55C, DHW Non Keep Warm, 50°C DHW
32a | DH/70C, DHW Non Keep Warm response time, 55°C DHW | 32a | DH/70C, DHW Non Keep Warm response time, 50°C DHW
32b | DH/60C, DHW Non Keep Warm response time, 50°C DHW | 32b | DH/55C, DHW Non Keep Warm response time, 50°C DHW